## Slide 1: An Industrial-Grade Power Generation, Management and Distribution System for Lunar Surface Applications
A Design Study for
Desert Fox Engineering Services Company
by the
sysRAND Corporation
Space Resource Roundtable IX 2007

## Slide 2: Proposed System Requirements
The primary source is a 150kwth Nuclear Reactor
Six Free Piston Stirling Engine (FPS) Alternators
Each FPS has two windings which split the load redundantly
Assume an efficiency of 28% the alternator output is ~42kwe
The transmission line extends at least a kilometer from the plant
The end-user consumer requires 120VDC
The system requires high reliability parts in an environment which includes reactor and high ambient radiation sources

## Slide 3: DC Mains / Rectified Alternators
Six FPS Dual-Tap Alternators
  Aggregate of 42KWe
Load Options:
  +2.5KV, -2.5KV & 5KV
Simple Current Summation
  Load Balanced to extent that individual path impedance allows
Return Cable 2x current
Eliminates alternator ‘sync’

## Slide 4: AC Mains
Six FPS Dual-Tap Alternators
  Aggregate of 42KWe
Load Options:
  Single, Two and Three-Phase(Δ)
Simple Current Summation
  Load Balanced to extent that individual path impedance allows
Discards Source Rectifiers
Back EMF ‘syncs’ alternators
Additional set of line filters for 3-phase

## Slide 5: DC Mains / Rectified Alternators
Requires a ‘chopper’ to invert DC Mains to Pulsed DC (not a sinewave)
Increases complexity for user sink circuits

## Slide 6: AC Mains / Rectified Alternators
AC Mains reduce the amount of circuitry where it counts – at the many taps which consume power – mostly through the elimination of inverters.

## Slide 7: Comparative Circuit Complexity
The AC system has fewer active components and more passive filters
The AC system requires less support hardware, such as cooling and cabinets
With fewer mode translations the AC system is more efficient, delivering a larger fraction (15% to 20% more) of the alternator output to the end-user
transmission lines

## Slide 8
One example of a high-power safety circuit uses the rectifiers as circuit breakers
Cathode current is sensed and compared to programmed thresholds
One of the grids is used to turn-off the tube in the event of a fault condition
Safety Circuits

## Slide 9
Another example of a high-power safety circuit uses temporary resistive loads
Using transient loads reduces load-switching-induced noise which causes ringing
Reducing ringing also reduces the ‘hunting’ by alternators trying to match output to load
Safety Circuits

## Slide 10
The GS-35B Power Triode is equivalent to an EIMAC (Varian) 3CPX1500A7 and is a typical high-current, high-voltage device capable of 2.5kw
These technologies persist because of these features
Vacuum Tube Technology